## L101803601
IESNA:LM-63-2002
| [TEST] | L101803601
| [TESTLAB] | LIGHT | LABORATORY, | INC. | (www.lightlaboratory.com)
| [ISSUEDATE] | 2018-10-25
| [MANUFAC] | SIMPLY | LEDS,LLC
| [LUMCAT] | FLDRS-110W-XV-40K-T5-CL
| [LUMINAIRE] | ROADWAY | AND | AREA | LUMINAIRE | W/ | CLEAR | LENS
| [BALLASTCAT] | INVENTRONICS | EUD-150S350DTA
| [OTHER] | INDICATING | THE | CANDELA | VALUES | ARE | ABSOLUTE | AND
| [MORE] | SHOULD | NOT | BE | FACTORED | FOR | DIFFERENT | LAMP | RATINGS.
| [INPUT] | 119.97VAC, | 108.31W
| [TEST | PROCEDURE] | IESNA:LM-79-08
TILT=NONE
| 1 | -1 | 1 | 28 | 19 | 1 | 1 | 0.8 | 0.44 | 0
| 1 | 1 | 108.31
Rho | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55 | 57.5 | 60 | 62.5 | 65 | 67.5 | 70 | 72.5 | 75 | 77.5 | 80 | 85 | 90
Theta
0 | 1287 | 1305 | 1350 | 1413 | 1512 | 1650 | 1870 | 2101 | 2234 | 2314 | 2365 | 2394 | 2509 | 2708 | 2975 | 3337 | 3746 | 4071 | 4392 | 4517 | 4194 | 3562 | 2635 | 1733 | 967 | 488 | 117 | 0
5 | 1287 | 1304 | 1351 | 1415 | 1511 | 1647 | 1872 | 2098 | 2229 | 2311 | 2363 | 2394 | 2507 | 2707 | 2975 | 3335 | 3746 | 4071 | 4400 | 4544 | 4241 | 3613 | 2697 | 1774 | 993 | 499 | 122 | 0
10 | 1287 | 1304 | 1349 | 1418 | 1507 | 1647 | 1867 | 2095 | 2235 | 2313 | 2361 | 2392 | 2509 | 2708 | 2976 | 3330 | 3733 | 4068 | 4409 | 4591 | 4354 | 3744 | 2844 | 1891 | 1071 | 530 | 127 | 0
15 | 1287 | 1304 | 1349 | 1417 | 1507 | 1642 | 1863 | 2083 | 2230 | 2317 | 2373 | 2397 | 2506 | 2697 | 2959 | 3312 | 3717 | 4054 | 4426 | 4654 | 4515 | 3976 | 3115 | 2117 | 1225 | 589 | 141 | 0
20 | 1287 | 1304 | 1348 | 1417 | 1508 | 1639 | 1854 | 2071 | 2229 | 2321 | 2384 | 2409 | 2506 | 2697 | 2954 | 3295 | 3700 | 4046 | 4458 | 4780 | 4752 | 4326 | 3525 | 2425 | 1481 | 684 | 156 | 0
25 | 1287 | 1303 | 1349 | 1416 | 1508 | 1636 | 1845 | 2058 | 2237 | 2334 | 2396 | 2418 | 2512 | 2693 | 2951 | 3292 | 3699 | 4064 | 4531 | 4987 | 5084 | 4833 | 4121 | 2885 | 1857 | 845 | 199 | 0
30 | 1287 | 1304 | 1348 | 1416 | 1508 | 1634 | 1840 | 2052 | 2239 | 2351 | 2418 | 2438 | 2524 | 2708 | 2971 | 3317 | 3732 | 4120 | 4656 | 5285 | 5556 | 5561 | 4967 | 3583 | 2399 | 1073 | 246 | 0
35 | 1287 | 1304 | 1347 | 1416 | 1507 | 1631 | 1837 | 2052 | 2250 | 2384 | 2452 | 2467 | 2544 | 2728 | 2997 | 3356 | 3787 | 4193 | 4792 | 5627 | 6097 | 6311 | 5775 | 4208 | 2729 | 1302 | 280 | 0
40 | 1287 | 1304 | 1349 | 1417 | 1510 | 1630 | 1835 | 2054 | 2268 | 2417 | 2477 | 2486 | 2565 | 2754 | 3026 | 3394 | 3839 | 4259 | 4892 | 5883 | 6505 | 6777 | 6051 | 4563 | 2816 | 1553 | 300 | 0
45 | 1287 | 1304 | 1349 | 1419 | 1511 | 1630 | 1831 | 2059 | 2281 | 2439 | 2494 | 2494 | 2575 | 2765 | 3038 | 3411 | 3861 | 4291 | 4934 | 5984 | 6682 | 6841 | 5854 | 4800 | 2984 | 1769 | 313 | 0
50 | 1287 | 1303 | 1349 | 1419 | 1512 | 1631 | 1835 | 2055 | 2278 | 2442 | 2482 | 2492 | 2576 | 2763 | 3030 | 3399 | 3848 | 4273 | 4901 | 5907 | 6521 | 6480 | 5532 | 4924 | 3067 | 1654 | 297 | 0
55 | 1287 | 1304 | 1350 | 1419 | 1512 | 1633 | 1839 | 2058 | 2269 | 2439 | 2466 | 2481 | 2568 | 2745 | 3012 | 3368 | 3804 | 4209 | 4812 | 5708 | 6062 | 5774 | 5254 | 4786 | 2897 | 1381 | 255 | 0
60 | 1287 | 1305 | 1351 | 1420 | 1514 | 1639 | 1848 | 2063 | 2271 | 2429 | 2451 | 2465 | 2553 | 2729 | 2986 | 3335 | 3758 | 4146 | 4716 | 5444 | 5473 | 4934 | 4824 | 4205 | 2355 | 1103 | 239 | 0
65 | 1287 | 1305 | 1351 | 1422 | 1516 | 1644 | 1856 | 2068 | 2277 | 2423 | 2434 | 2451 | 2543 | 2721 | 2977 | 3314 | 3723 | 4110 | 4654 | 5173 | 4871 | 4192 | 4262 | 3458 | 1836 | 877 | 202 | 0
70 | 1287 | 1306 | 1352 | 1423 | 1517 | 1652 | 1865 | 2076 | 2287 | 2417 | 2420 | 2438 | 2534 | 2715 | 2973 | 3313 | 3716 | 4103 | 4607 | 4939 | 4396 | 3775 | 3960 | 2947 | 1449 | 712 | 183 | 0
75 | 1287 | 1307 | 1354 | 1424 | 1521 | 1658 | 1875 | 2084 | 2297 | 2412 | 2410 | 2435 | 2535 | 2718 | 2974 | 3317 | 3729 | 4112 | 4577 | 4745 | 4063 | 3598 | 3779 | 2553 | 1178 | 597 | 157 | 0
80 | 1287 | 1306 | 1354 | 1425 | 1521 | 1664 | 1882 | 2094 | 2305 | 2411 | 2403 | 2434 | 2537 | 2718 | 2976 | 3322 | 3742 | 4127 | 4571 | 4605 | 3846 | 3518 | 3614 | 2255 | 1022 | 529 | 142 | 0
85 | 1287 | 1307 | 1353 | 1426 | 1523 | 1668 | 1890 | 2105 | 2314 | 2410 | 2405 | 2434 | 2536 | 2716 | 2976 | 3323 | 3750 | 4135 | 4560 | 4516 | 3725 | 3477 | 3496 | 2075 | 939 | 497 | 137 | 0
90 | 1287 | 1305 | 1354 | 1425 | 1523 | 1667 | 1894 | 2110 | 2318 | 2410 | 2404 | 2433 | 2536 | 2716 | 2980 | 3316 | 3749 | 4133 | 4558 | 4486 | 3685 | 3463 | 3445 | 2016 | 911 | 486 | 136 | 0
Average | 1287 | 1304.6316 | 1350.3684 | 1419.3158 | 1513.0526 | 1644.3158 | 1857.7895 | 2075.5789 | 2265.6842 | 2383.8947 | 2418.8421 | 2439.5789 | 2535.5263 | 2721.3684 | 2984.5263 | 3336.1053 | 3756.7895 | 4136.0526 | 4623.4737 | 5072.3684 | 4980.1053 | 4671.3158 | 4197.3684 | 3115.6842 | 1798.7368 | 903.5789 | 197.3158 | 0
Steradians | 0 | 0.023909 | 0.071546 | 0.11864 | 0.16483 | 0.20976 | 0.2531 | 0.29451 | 0.1621 | 0.17159 | 0.18075 | 0.18957 | 0.19802 | 0.2061 | 0.21379 | 0.22107 | 0.22793 | 0.23436 | 0.24034 | 0.24586 | 0.25092 | 0.25549 | 0.25959 | 0.26318 | 0.26628 | 0.26887 | 0.54345 | 0.54762 | 6.2832 | Total Steradians=2*PI()
Lumens | 0 | 31.193 | 96.6138 | 168.3857 | 249.3936 | 344.9168 | 470.2096 | 611.2871 | 367.263 | 409.045 | 437.2034 | 462.4641 | 502.0963 | 560.8871 | 638.0702 | 737.5256 | 856.3002 | 969.3267 | 1111.2082 | 1247.109 | 1249.5977 | 1193.4977 | 1089.5767 | 819.9927 | 478.9637 | 242.9421 | 107.2309 | 0 | 15452.3001 | Total Lumens
[29 empty] | 15931 | Reported Lumens
[29 empty] | 3.0048 | % Error